## Sheet1
Technical Parameters for 1500W Pure Sine Wave Inverter
Model | PA1500W-12V | PA1500W-24V | PA1500W-48V
Output power | 1500W
Peak power | 3000W
Input voltage(Range) | DC12V（9.5-15.5V） | DC24V（19-31V） | DC48V（38-61V）
Output voltage(Single) | （100VAC/110VAC/120VAC/220VAC/230VAC/240VAC）±5%
Unload current less than | ≤0.6A | ≤0.3A | ≤0.2A
Output frequency | 50Hz or 60Hz
Output waveform | Pure Sine Wave
Waveform distortion | THD≤3%( Pure resistive Load))
USB | 18W Fast charging |  | /
Max.output efficiency | 88% | 90% | 92%
Low voltage protection | Pre-alarm (alarm off after 1 sound), LED Red light on, voltage contiously reduce and shutdown
Over voltage protection | Pre-alarm (alarm off after 2 sounds), LED Red light on, shutdown
Over load protection | Continuous alarm, LED Red light on, shutdown
Over temperature protection | Pre-alarm (alarm off after 3 sounds), tempurature continously rise, LED Red light on, shutdown
Short circuit protection | Perfect protection and no damage the circuit
Input reverse polarity protection | Fuse burn-out
Low voltage alarm | 10.5±0.5V | 21±0.5V | 42±1V
Low voltage protection | 9.5±0.5V | 19±0.5V | 38±1V
Over voltage protection | 15.5±0.5V | 31±0.5V | 61±1V
Low voltage recover | 13±0.5V | 24±0.5V | 48±1V
Over voltage recover | 14.5V±0.5V | 29V±0.5V | 58V±1V
Working temperature | -20°- +50°
Product Dimension(mm) | 400*180*85
Mounting Size(mm) | 375*100
Product Lable Size(mm) | 350*60
Packing(mm) | 490*240*150
Net./gross weight(kgs) | 3.86/4.3
QTY/CTN | 4 PCS
Meas./CTN(mm) | 510*500*350
Gross weight/CTN(kgs) | 18.2
Warranty | 24Months
DC Cable(mm²) | 16 | 10 | 4
Cooling method | Intelligent air cooling
Note: Our products update constantly.The technical parameter is for reference only.Please refer to our real product.